###### TS-I-D-YY
Duct temperature transmitter

Features

- Temperature measurement for air ducts.

- Simple and secure installation

- Wide range of temperature probes

- 4…20mA measuring signals

- Compact size and modern design

Applications

- On return air ducts to measure heating/cooling return air

- On supply air ducts to measure heating/cooling supply air

- In heat exchangers and air handling units to control heating/cooling coils for temperature and humidity control

- As frost protection sensor

Temperature Transmitter

The transmitter measures the temperature by the use of a PT1000 sensing element. The transmitter analog output may be 4-20mA. And the transmitter include a noise filter. the power supply is large range DC18V----DC30V .Standard temperature measurement range is 0…50 °C.

linearity Signal output:

TIMAX

TIMin

Y [%]

100%

0%

T [°C, °F]

## Ordering

Ordering number: TS-I1-D-YY

-I indicates the transmitter signal out is 4 -20mA.

YY indicates the probe length. Standard probe length is 15cm.

For example:TS-I1-D-15

The duct temperature transmitter signal out is 4 – 20mA ,and the probe length is 15cm, range is 0 -100℃.

## Installation

Duct probes should be installed directly on the duct, in an area where the air stream is well mixed:

- Locate a supply air sensor two or three meters down stream from the nearest fan and coil.

- Mount the return air sensor close to the air inlet but downstream from a return fan if one is present.

- To install the sensor, assemble base plate and probe, then drill a 8 mm hole and two 3 mm holes on a diameter of 25 mm in the duct.

- Use two self-tapping sheet metal screws to tighten the mounting circuit in the cover.

- Connect the wires according to the wiring diagram to the measuring circuit in the cover:

  - If the transmitter signal out is 0-10V,it’s need three terminal connections,DC24V,Ground and signal out.

  - If the transmitter signal out is 4-20mA,it’s need two terminal connections,DC24V,Ground and signal out.

  - The connection signal cable should be shield wires.

- Assemble the cover with the mounting plate.

- Insert the assembled probe through the center opening of the mounting plate into the air stream.

- Tighten the horizontal screw on the mounting plate to fix the probe to the duct.

## Technical Specification

| Power supply | Option voltage | DC18V---DC30V |
| --- | --- | --- |
|  | Power Consumption | Max 2 VA |
| Signal outputs | -U type | 4 – 20 mA |
|  | accuracy | 0.5% |
|  | Temperature range | TS-I-D-15 ：0 - 50℃ TS-I1-D-15 ：0 - 100℃ TS-I2-D-15 ：0 - 200℃ TS-I3-D-15 ：-20 - 60℃ |
| Connection | Connection Terminals | 2.5 mm2 |
| Environment | Operation Climatic Conditions Temperature Humidity | To IEC 721-3-3 class 3 K5 -40…70°C <95% r.h. |
|  | Transport & Storage Climatic Conditions Temperature Humidity Mechanical Conditions | To IEC 721-3-2 and IEC 721-3-1 class 3 K3 and class 1 K3 -40…80°C <95% r.h. class 2M2 |
| Standards | conform according to EMC Standard 89/336/EEC EMEI Standard 73/23/EEC | EN 61 000-6-1/ EN 61 000-6-3 |
|  | Automatic electrical controls for household and similar use Special requirement on temperature dependent controls | EN 60 730 –1 EN 60 730 – 2 - 9 |
|  | Pollution Class | Normal acc. To EN 60 730,RoHS compliant |
|  | Degree of Protection | IP56 to EN 60 529 |
|  | Safety Class | III (IEC 60536) |
| Housing Materials | Cover & Mounting Plate Probe | Fire proof ABS plastic Stainless Steel |
| General | Dimensions [mm] | Cover: 42 x 112 x 88 (H x W x D) Probe: ø 6 x 200 (Diameter x L) |
|  | Weight (including package) | 135g |

## Wire diagram

1

2

+24

OUT

Terminal  connections:

Power supply DC24V

Temperature singal output 4-20mA

dimension [mm]